SENSITIVITY ANALYSIS TAKING INTO CONSIDERATION THE LOWEST ENERGY COST FROM A COMBINED SYSTEM OF CONSUMPTIONAL WATER HEATING

# Vladimir Medica, Bernard Frankovic, Branimir Pavkovic

Faculty of Engineering, University of Rijeka,

51000 Rijeka, Vukovarska 58, Croatia

ABSTRACT. Consumptional water heating for tourist facilities and domestic use is a significant  energy consumer. It is advisable to use solar energy for this purpose, especially in coastal regions. The combined system for consumptional water heating in tourist facilities is chosen using a developed simple procedure, based on average monthly solar radiation and temperature data. The optimal system configuration depends on consumptional dynamics, solar radiation and the type of auxiliary heating system, as well as prices of energy and equipment. The system consists of solar collectors combined with either electric heater, oil fired boiler or heat pump. Software has been developed to perform a selection of optimal systems and sensitivity analysis. The paper presents a sensitivity analysis regarding the influence of changes in equipment, service and energy costs incurred due to changes in the inflation rate, interest rate and considered period on the selected optimal combined system. This analysis points out the permitted deviations in solar equipment investment costs to keep the solar system still optimal when compared with other systems. A heat pump system is shown to be the most convenient compared to other consumptional water heating systems. The presented analysis enables decision making during the system operation period as well as during project development.

1. INTRODUCTION

The consumptional water heating has always been considered as the most feasible solar energy application, but nowadays even that application feasibility is doubtful as a result of expensive equipment. The economic analysis and optimization are required to enable decisions be made about solar energy utilization. Random characteristic of solar radiation demands additive heating in solar systems. A choice must be made between heating with conventional boiler, electric heater or heat pump alone or any of those three combined with solar collectors. System produced energy costs (investment, energy, maintenance and the market conditions) depend on that decision. Extensive calculations are necessary in order to find out an optimal combination and this implies the use of computer programs. A considerable number of input parameters is necessary to analyze dynamic behavior of the solar heating system in supposed market conditions for the considered period. Besides the physical factors, the market conditions which are rather turbulent, will affect the optimum system configuration giving the lowest energy cost. To analyse the sensitivity of the system parameters on market conditions, software was developed. The influence of system life period, the specific solar collector system price, the interest rate and inflation rate to the otpimum system configuration was analyzed. From this analysis, system sensitivity to market conditions could be deduced.

2. THE MATHEMATICAL MODEL

Energy for consumptional water heating is calculated for every month, and later summarized for the whole year, the number of guests during the month considered, specific daily consumption of hot water per guest, hot water temperature and entering cold water temperature are known. Details of the mathematical model are presented in the reference 1.

From the energy consumption records, the required solar collector area was determined. This area depends on the collector surface orientation and solar radiation to tilted surface 2. The components of solar radiation are determined using correlations 3 for diffusive component, while the beam component was determined from extraterrestrial solar radiation on a hourly basis and averaged for a month analyzed. A daily average of extraterrestrial radiation was achieved by summarizing the hourly irradiation (only when the panel is exposed) and dividing the sum with the number of days in the month considered. The solar radiation to the tilted collector surface was calculated using the ratio between beam radiations to tilted surface and to the horizontal surface. The value of this ratio was averaged during the month considered. Collector efficiency was calculated using manufacturer correlations.

In the combined system for consumptional water heating, solar collectors are combined with additive heating, such as heat pump, electric heater or oil fueled boiler, as shown in Fig. 1.

Figure 1. Combined system for consumptional water heating

A simple heat pump model was adopted, taking into account influence of evaporation and condensing temperatures on the performance coefficient, according to 4. Efficiency is achieved from 5 by polynomial regression. Evaporating temperature depends on the heat source selected. In the present analysis, ambient air was chosen as the heat source. The compressor work was evaluated by heat demand and heat pump parameters. With daily operation time, the compressor power was found. In the case of oil fired boiler heating, the fuel consumption was determined from the heat consumption, fuel lower heat value and boiler efficiency. In the same manner as above, the boiler size can be determined knowing the operation time.

When electric heating is applied, only the heater efficiency has to be considered to evaluate  energy consumption for heat production. Electric power is achieved by dividing energy consumption with operation time.

According to the annuity model [3] total costs K for a system are determinated by the equipment price Kc(from known equipment size), cost of energy consumption Ke and maintenance costs Kmas

K=Kc+Ke+Km  .                                                                                              (1)

The expression for capital cost is Kc=I1−ra, where I is total amount of investment, which was determinated during the program operation by multiplying values for collector area, boiler and electric heater power or the heat pump´s compressor power with specific user defined prices of equipment.

With factor r we take into account the lifetime of the equipment l, which can be different than the period of consideration c. The multiplier qe=1+ew100 takes into account price increase for the new equipment and ew is the yearly rate of that increase. With multiplier q=1+i100 we consider the interest rate i. Annuity factor a is given as a=qtcq−1qtc−1.

Energy costs are calculated depending on the energy source used. If oil is used, energy costs for the first year are given as product of oil consumption Band specific fuel price Pb. As regards the period c energy costs are:

Ke=BPb⋅d⋅a                                                                                                   (2)

First year costs for electric energy are achieved as the sum of consumed energy costs and power costs, and average yearly costs during the period c:

Ke=EPe+EmaxPp⋅d⋅a                                                                            (3)

where E is energy consumed during the year, Pe is unit price of that energy, Emax (or in the case of heat pump Wmax) installed electric power of equipment and Pp electric power unit price.

Inflation influence (increasing energy costs) is taken through discount factor d=qτc−qkeτcqτcq−qke   with factor qke=1+p100 and with p as the inflation rate.

Maintenance costs can be calculated as Km=mI⋅d⋅a, where with (mI) the first year maintenance costs are denoted (as the product of the percentage m of maintenance costs in investment I). With d discount factor is denoted and with a the annuity factor.

3. EXAMPLE OF CALCULATION RESULTS

The analysis has been performed in the following manner:

An optimal collector tilt (30 degrees, facing southwards) is determined in the first step for each consumer - a tourist camp and hotel at location Lošinj in Croatia, both designed to accommodate 500 persons. The camp was used only during the summertime, while the hotel was in operation throughout the year. Daily hot water consumption per person was set at 35 l for camp and 150 l for the hotel. Hot water temperature was set at 45oC. Energy consumption is shown in Fig. 2.

Figure 2. Energy for consumptional water heating during a year for camp and hotel in Lošinj

Further analysis has been performed to determine the optimal heating system under variable market conditions. Inflation rate was varied from 0 to 20%, interest rate was varied from 4 to 20%, and collector system unit price from 200 to 600 DEM/m2. Energy and equipment prices taken into consideration were at price level in Croatia 1998. Average electric energy cost was 0,08 DEM/kWh and electric power cost 11 DEM/kW monthly. EL fuel oil cost was 0,77 DEM/kg. Electric heater price was 60 DEM/kW, boiler price (including pipes, fuel storage, automatic control, pumps, boiler house) was 200 DEM/kW, air to water heat pump price was 1500 DEM/kW of compressor power. Lifetime of equipment and consideration period were varied from 10 to 20 years, both equal. Collector type was single glazed, with flat absorber, η=0,75−6,34ΔT/I.

First year maintenance costs were 2% of investment for collectors, 4% for boiler, 5% for heat pump and 3% for electric heater. In 1 results were achieved which indicated the cost structure for different systems.

The program proposed in this paper facilitates an analysis of the influence of variation in market conditions on the choice of a optimal system as well as a sensitivity analysis.

Figure 3 presents the results of combined system optimization regarding the lowest energy cost for hotel and camp.

0

100

0

0.5

DEM/

kWh

A/Amax

%

20

Interest

%

4

20

Inflation, %

200 DEM/m2

0

0

100

0

0.5

DEM/

kWh

A/Amax

%

20

Interest

%

4

20

Inflation, %

350 DEM/m2

0

0

100

0

0.5

DEM/

kWh

A/Amax

%

20

Interest

%

4

20

Inflation, %

500 DEM/m2

0

## Hotel

0

100

0

0.5

DEM/

kWh

A/Amax

%

20

Interest

%

4

20

Inflation, %

200 DEM/m2

0

0

100

0

0.5

DEM/

kWh

A/Amax

%

20

Interest

%

4

20

Inflation, %

350 DEM/m2

0

0

100

0

0.5

DEM/

kWh

A/Amax

%

20

Interest

%

4

20

Inflation, %

500 DEM/m2

0

Heat pump

Heat pump + collector

Collector only or mostly

Camp

Figure 3 Solar collector area, energy cost and combined system type for lowest energy cost considering solar collector system unit price, interest rate and inflation rate for hotel and camp. Period of consideration was set for 15 years

In the upper part of fig. 3 the ratio of used solar collector area as regards maximum required collector area (for water heating only with solar collectors) is presented. In the centre of figure 3 the energy cost is presented. On the lower part, various patterns indicate the optimal combined system type. From figure 3, it is evident that the increase of the interest rate has moderate influence on the lowest energy cost rise, mainly affected by the influence of the investment cost. As opposed to this, the increase of the inflation rate has higher influence on the energy cost rise. When comparing the camp and hotel, the higher energy cost for camp is evident, because of the limited period of energy utilization. For both, camp and hotel, it can be concluded that the solar collectors are more convenient in market situations with high inflation and moderate interest rate. Increasing the solar collector system unit price gives an advantage to the heat pump alone or combined with solar collectors. In a situations with low inflation rate and high interest rate, the heat pump alone has no competitors in energy cost.

The solar collectors are more convenient in energy production when the lifetime of equipment and period of consideration (which are assumed with the same value in the presented example) are longer.

4. CONCLUSION

The domination of solar collectors is favored by lowering the unit price of solar collector system and the interest rate and by increasing the inflation rate, the component life time and considered period. The prognosis of efficient application limits for solar collectors in various market conditions is given.

# REFERENCES

# 1 Pavković B., Medica V.: Optimization of solar consumptional water heating systems based on average monthly data, Proceedings of the III. International Congress SITHOK, Maribor, SLOVENIA. May 1998., p. 243-251

2  Duffie, Beckmann: Solar Engineering of Thermal Processes, J. Willey, New York, 1980.

3 Von Cube, H. L.:Handbuch der Energiespartechniken, Bd. 1, 2, 3. Verlag C. F. Muller, Karlsruhe 1983.

4  Rietschel, Reiss: Heiz und Klimatechnik, Springer Verlag Berlin, 1968.

5  Garms, M.: Handbuch den Heizungsingenieur, Bd. 1, VEB Verlag, Berlin, 1969.

6  Pavković, B.: Optimalizacija korištenja obnovljivih izvora energije upotrebom dizalice topline, Magistarski rad, Tehnički fakultet Sveučilišta u Rijeci, 1993.