A GLOBAL APPROACH OF AIR CONDITIONED INDOOR ENVIRONMENT QUALITY CONSIDERING THERMAL 
COMFORT, ACOUSTIC COMFORT AND AIR DIFFUSION

E. Rutman1, C. Inard2, I. Viličić3, B. Franković3, A. Bailly1

1CIAT, Avenue Jean Falconnier 01350 Culoz, France

tel : +33(0)479424216, fax : +33(0)479424013, e.rutman@ciat.fr, a.bailly@ciat.fr

2Leptab, La Rochelle University, Av Michel Crepeau 17042 La Rochelle Cedex France

tel : +33(0)546457246, fax : +33(0)546458203, cinard@univ-lr.fr

3Faculty of Engineering, University of Rijeka, Croatia

tel : +385(051)675801, fax : +385(051)701470, intel-trade@ri.tel.hr

Abstract: An experimental study on real HVAC system and their optimimisation to reduce local discomfort in a climate chamber has been presented. First, general characteristics such as separation distance of cold wall jets and maximum velocity and temperature decay have been analysed. Then the analyse of discomfort due to thermal effect, acoustic effect and air diffusion effect in accordance to air flows characteristics has been carried out. An economic parameter was included to present a general approach of the global comfort.

Key words: Air conditioned offices, horizontal cold air jet, thermal comfort, acoustic comfort, air quality diffusion, experiment, HVAC system.

1. INTRODUCTION

The occupants of offices are submitted to various local discomforts, Fanger [1] due to temperature, draft and noise. To improve comfort in buildings different kinds of HVAC systems are often used. In summer the cold air is introduced into the room by HVAC system, like the resulting air velocity and temperature distribution within the occupied zone is as uniform as possible to minimise local discomfort. Thus, in air conditioned-spaces, the cold air jet and plumes due to internal loads are usually the main driving flows. So, before discussing comfort conditions, the driving flows and specially the provided cold air jet laws has to be described. The purpose of this experimental work is to confirm the cold air jet characteristics and a global approach of comfort which takes into account thermal and acoustic comfort including air diffusion.

2. EXPERIMENTAL APPARATUS AND CONDITIONS

The measurements, Rutman [2] were carried out in the CIAT’s laboratory located in Culoz, France. Figures 1 and 2 present the longitudinal section of our experimental test chamber. The volume is equal to 5.20x4.05x2.50 m3 bounded on five sides by air volumes regulated at a constant temperature level. The sixth side is submitted to the influence of a climatic housing, where we can simulate external air temperature variation. For these experiments, the value of

the external temperature was set at + 30 °C. Furthermore, we simulate the presence of real internal heat loads, including computer, and human bodies. These thermal heat loads are balanced by fan coils unit mounted on the ceiling. Two fan coils unit, unit 1 and unit 2 were tested. The dimensions of the unit 1 supply grille are 1.19 x 0.091 m2 and the unit 2 supply grille is variable from 0.34 x 0.036 m2 to 0.34 x 0.072 m2 therefore the unit 2 has simultaneous 4 directions for the airflow. In the jet, the air velocity and the relative intensity of velocity turbulence are measured with a Dantec Laser Doppler Anemometer unidirectional system. The temperature was measured with a Newport Omega, 0.051 mm diameter, K-type thermocouple calibrate at the CIAT laboratory. For simultaneous measurements of velocity and temperature, were used a “Quatuor Industrie” two dimensional displacement device. For each unit, 8 tests with various supply conditions were carried out. Two mechanical configurations of fan coils have been tested. For unit 1, the first one, the air jet has one supply direction, for the second one, three directions for the airflow. For unit 2, the direction of the jet is to the ceiling (summer position) then to the floor (winter position). Secondly, we modified the airflow rate, and we adapted the water conditions in order to get an operative temperature in the occupancy zone equal to 24.5°C  1.5°C. Tables 1 and 2 give the parameters used for the experiments. For the comfort, the air velocity, the relative intensity of velocity turbulence and temperature in the occupied zone of the room are measured with a thermoanemometric sensor, (type DANTEC 54T21) placed at 76 different locations in the occupancy zone. Vertical test point located at 0.1m for foot, 0.6 m for hip, 1.1 m for head of a sitting occupant and 1.7 m for head of a standing occupant, ASHRAE [3]. This probe has been calibrated by DANTEC. The inner wall surface temperatures are measured with thermocouples type K calibrated at the CIAT laboratory. The acoustical level is measured with a microphone sensor type Bruel & Kjaer 4189 and a frequency analyser type Kontron FFT-AD3524. To calibrate the microphone, we used a pistonphone type Bruel & Kjaer 4231. For acoustic measurements, we placed our probe at 36 different locations in the occupancy zone.

Figure 1. Longitudinal section the experiment cell and the unit1

# Figure 2. Longitudinal section the experiment cell and the unit 2

# Table 1. Experimental conditions, unit 1

| Test N° | Number of | Q0 | U0 | T0 | T0 | Ar0 | Re0 | LT |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | supply direction | m3/h | m/s | °C | °C | x103 |  |  |
| 1 | 1 | 736 | 5.9 | 24.5 | 0.0 | 0.00 | 32737 | - |
| 2 | 1 | 732 | 5.5 | 14.1 | 9.1 | 0.91 | 30517 | 5.7 |
| 3 | 1 | 537 | 4.5 | 11.0 | 12.5 | 1.87 | 24969 | 3.9 |
| 4 | 1 | 366 | 3.0 | 12.5 | 12.1 | 4.05 | 16646 | 2.7 |
| 5 | 3 | 670 | 5.8 | 24.5 | 0.0 | 0.00 | 32182 | - |
| 6 | 3 | 722 | 5.6 | 11.8 | 11.8 | 1.14 | 31072 | 5.0 |
| 7 | 3 | 532 | 4.2 | 12.1 | 12.7 | 2.17 | 23304 | 3.7 |
| 8 | 3 | 366 | 2.9 | 11.5 | 13.5 | 4.85 | 16091 | 2.4 |

# Table 2. Experimental conditions, unit 2

| Test N° | Supply | Q0 | U0 | T0 | T0 | Ar0 | Re0 | LT |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | direction to | m3/h | m/s | °C | °C | x103 |  |  |
| 9 | Ceiling | 462 | 5.3 | 24.1 | 0.0 | 0.00 | 36846 | - |
| 10 | Ceiling | 684 | 5.8 | 15.6 | 8.5 | 0.97 | 41050 | 3.6 |
| 11 | Ceiling | 623 | 5.2 | 16.3 | 7.8 | 1.08 | 37063 | 3.4 |
| 12 | Ceiling | 570 | 4.7 | 16.3 | 8.4 | 1.44 | 33240 | 2.9 |
| 13 | Floor | 472 | 4.2 | 24.1 | 0.0 | 0.00 | 43161 | - |
| 14 | Floor | 725 | 5.6 | 14.5 | 9.1 | 1.64 | 58620 | 4.1 |
| 15 | Floor | 623 | 5.1 | 14.1 | 9.3 | 2.07 | 52887 | 3.6 |
| 16 | Floor | 560 | 4.2 | 14.5 | 10.2 | 3.27 | 44090 | 2.9 |

The Archimedes number, Ar0 = gT0 A00.5/U02 , the Reynolds number Re0=U0 A00.5/  and the thermal lenght LT = (A0 / Ar0)0.5 are used to characterise the supply conditions. We used the square root of the supply area (A0) because the ratio effective length (l0) / effective width (h0) is equal to 13 for unit1 and is variable from 9 to 5 for unit 2. These values are a characteristic of a three dimensional jet. Mean values of the exit temperature, T0 and velocity, U0 are obtained by measuring the temperature and velocity profiles over a 12 x 25 mesh ( y = 47 mm and z= 5 mm). The integration of the velocity profiles over the grille area allows to calculate the air mass flow rate, Q0 of the fan coil. The relative differences between these values and those obtained with a standard measurement of airflow, ISO [4] are less than 7 %.

3. RESULTS AND DISCUSSION

Firstly, the main results presented here consist in the maximum velocity and temperature decays in the horizontal wall jet. The separation distance of the horizontal jet according to the inlet conditions was presented. Secondly, the results presented here consist in the ISO noise level, ISO [5], the ADPI index, Koestel [6], the floor temperature, the vertical air-temperature difference between 0.1m and 1.1 m and between 0.1 m and 1.7 m, the DR index, ISO [7] and the PPD index,  ISO [7].

3.1. Cold air jet characteristics

Figures 3 and 4 present the decay of the centerline velocity, Um and temperature, Tm for unit1. Usually, four distinct regions may be defined for a wall jet, as discussed by Hassani and al [8] : the core zone, the characteristic zone, the transition zone and the fully established turbulent zone. The centerline velocity and temperature decays of the jet are given by:

Um / U0  = KV [1 / (x+x0)]nV    								(1)

Tm / T0 = KT [1 / (x+x0)]nT								(2)

The parameter x0 is the virtual origin of the wall jet. Values of nV and nT depend of the zones discussed before. Tables 3 and 4 give the values obtained in this study.

# Table 3. Centerline velocity and temperature decay coefficients, unit1

| Number of supply direction | KV | nV | Correlation coefficient | KT | nT | Correlation coefficient |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 0.6 | 0.3 | 0.73 | 1.0 | 0.3 | 0.75 |
|  | 1.6 | 0.9 | 0.85 |  |  |  |
| 3 | 0.5 | 0.3 | 0.75 | 1.3 | 0.9 | 0.85 |
|  | 1.2 | 0.9 | 0.95 |  |  |  |

Table 4. Centerline velocity and temperature decay coefficients, unit 2

| Supply direction to | KV | nV | Correlation Coefficient | KT | nT | Correlation coefficient |
| --- | --- | --- | --- | --- | --- | --- |
| Ceiling | 1.25 | 0.4 | 0.93 | 1.0 | 0.3 | 0.93 |
| Floor | 1.7 | 0.9 | 0.82 | 1.3 | 0.6 | 0.91 |

Figure 3. Velocity and temperature decay for the one direction jet, unit 1

# Figure 4. Velocity and temperature decay for the three direction jet, unit 1

If KV and KT are considered, for unit 1 a KT value higher than a KV value is obtained. Thus the ratio KT / KV is equal to 1.13 when the air jet has one direction and 1.66 when the air jet has three directions. The usual value of this ratio is 0.84 as discussed by Meslem [9]. The values obtained with our experiments implies that the thermal diffusion is higher than the dynamic diffusion as the velocity and temperature half widths, showed since z0.5U > z0.5T as discussed by Rutman [2]. It is difficult to give an explanation to these results. Nevertheless, considering that the ratio between the grille length lo and the climatic chamber length is equal to 1/3, we may assume that the influence of the confined space is high on the development of the jet. On the other hand we obtain for unit 2 usual values with the ratio KT / KV equal to0.76 and 0.80.

3.2. Separation distance of cold horizontal wall jet

The behaviour of the wall jets at separation is very complex as discussed by Hassani [8]. Figure 5 presents the separation distance XS for all experiments. We can notice that the experimental values Xs are close to Grimitlyn and al [10], Anderson and al [11] and Rodhal [12] values. Relations between the detachment point and the initial Archimedes number is given by:

Unit1 : Xs / A00.5 = 0.2 Ar0-0.6, the correlation coefficient is 0.91.			(9)

Unit2 : Xs / A00.5 = 0.1 Ar0-0.74, the correlation coefficient is 0.98.			(10)

Figure 5. Separation distance of cold jets

Experimental studies of airflow characteristics in an air-conditioned chamber were carried out under various conditions. A first analysis made on the decay of the centerline velocity and temperature show the influence of the confined space. In discordance with others authors, we noticed a thermal diffusion more important than the dynamic diffusion. So, future studies on jets issued from real HVAC systems in confined spaces are needed. Furthermore, we proposed a relationship between the separation distance of the cold jet and the initial Archimedes number.

## 3.3. Acoustic comfort

For this kind of office is accepted a noise level ISO value between 30 dB and 35 dB, ISO [5]. Table 5 shows for unit1 the number of location in the test room where the noise level comfort is satisfy. For test n° 3 and n° 6 we have always a good acoustic comfort, for test n° 2 and n° 5, we have only 50 % of location with an acceptable level and for test n° 1 and n° 4 there is no location with an acceptable level. So, for unit 2  due to a prototype of motors it cannot be obtained location with an acceptable acoustic level.

Table 5: Number of location where the noise level comfort is satisfy, unit1

|  | ISO level range |  |  |
| --- | --- | --- | --- |
| Test n° | < 30 dB | [ 30 dB ; 35 dB ] | < 35 dB |
| 1 | 0% | 0% | 100% |
| 2 | 0% | 50% | 50% |
| 3 | 94% | 6% | 0% |
| 4 | 0% | 0% | 100% |
| 5 | 0% | 50% | 50% |
| 6 | 94% | 6% | 0% |

## 3.4. Air diffusion performance index

The measured Effective Draft  Temperature EDT, Koestel [6] and ADPI index distribution in the climate chamber are shown on figure 6. For unit 1 the value of the ADPI fluctuates with the mechanical configuration of the fan coil. If we compare tests with a same supply flow rate, but not the same mechanical parameter, the APDI value is roughly divided by 2. For unit 2 the influence of the mechanical configuration is very low, then we obtain an ADPI value near to the optimun.

Figure 6. EDT distribution and ADPI values

### 3.5. Thermal Comfort

For our experiments, the percentage of location which satisfy the ISO 7730 for the floor temperature and the air-temperature difference between the head (1.7 m or  1.1 m) and the foot (0.1m) are always 100 %. Figure 7 presents the number of location in the test room where we can satisfy the ISO 7730, ISO [7] standard recommendation for the DR index and the PPD index. For unit1 when the thermal length increases the PPD index increases while the DR index decreases. It’s certainly due to the variation of the separation distance of the cold horizontal wall jet. For unit 2, mounting on the center of the ceiling, the PPD and DR indexes decrease with the thermal length. It’s certainly due to the 4 directions of supply air

wich provide a good repartition of velocity in the occupied zone but also important values of the turbulence of the velocity.

Figure 7. PPD and DR distributions

#### 3.6. A Global approach

Figure 8 shows for unit1 evolution of average values in the occupancy zone of PPD index, DR index, ISO level but also the electric comsuption of fan, pump and the compressor. It can be noticed that, with the Archimedes number as reference, each comfort parameter including the electric comsumption has is own evolution. Thus, the PPD index, the ADPI index and the electrical comsumption increase when the ISO level and the DR index decrease. The difficulties to optimize the reduction of the local discomfort with occupants preferences are printed out. In fact, the best way to analyze these kinds of experiments seems to be a multricriteria analysis.

##### Figure 8.  Evolution of global comfort criteria

4. CONCLUSION

Experimental studies of airflow characteristics in an air-conditioned chamber were carried out under various conditions. A first analysis made on the decay of the centerline velocity and temperature show the influence of the confined space. In discordance with others authors, a thermal diffusion more important than the dynamic diffusion was noticed. So, future studies on jets issued from real HVAC systems in confined spaces are needed. Furthermore, we proposed a relationship between the separation distance of the cold jet and the initial Archimedes number.

Then, a first analysis carried out on the thermal comfort and the quality of air diffusion showed the influence of the inlet Archimedes number and the separation distance of the cold horizontal wall jet. Lastly, it’s difficult to carryout a general law between all the indoor environment indexes. These work perspectives are the use of multicriteria analysis including the comfort indexes discussed previously.

## ACKNOWLEDGEMENTS

This study was supported in part by the Research and Technology National Agency (ANRT), the Environment and Energy Management Agency ( ADEME) and Electricity of France (EDF).

# REFERENCES

- Fanger, P.O.: Thermal comfort analysis and applications in environmental engineering, Mc Graw Hill, New-York, U.S.A, 1970

- Rutman, E.: Contribution à l’évaluation de la qualité des ambiances intérieures climatisées, These de Doctorat , Université de la Rochelle, La Rochelle, France, 2000

- ASHRAE (1992). Thermal environmental conditions for human occupancy. ANSI/ASHRAE standard 55, Atlanta, U.S.A.

- ISO Ventilateurs industriels-Essais aérauliques sur circuit normalisés. ISO standard 5801:1997(F), ISO Geneva, Switzerland, 1997

- ISO: Assessments of noise with respect to community respons, Technical comitee ISO/TN43, Geneva, Switzerland, 1971

- Koestel, A., Tuve, G.: Performance and evaluation of room air distribution systems, ASHRAE Trans.61, 1955, 533-550.

- ISO: Moderate thermal environments. Determination of the PMV and the PPD indices and specifications of the conditions for thermal comfort, ISO standard, Geneva, Switzerland, 1995

- Hassani, A., Kirkpatrick, A. and Sforza, P.: Flow and separation Characteristics of three-dimensional Negatively Buoyant Wall Jets, HVAC&R RESEARCH 3:2, 1997, 112-127.

- Meslem, A., Beghein, C., Inard, C., Allard, F.:Lois de décroissance d'un jet turbulent ridimensionnel vertical de paroi impactant à forces de poussée défavorable", Int. Comm. Heat Mass Transfer, vol. 26, 1999, No. 4, pp. 487-498.

- Grimitlyn, M.I., Pozin, G.M.: Fundamentals of optimising air distribution systems. ASHRAE Transaction 99:1, 1993, 159-1365.

- Aderson, R., Hassani, V., Kirkpatrick, A., Knappmiller, K. and Hittle, D.: Experimental and computational visualisation of cold air ceiling jet, ASHRAE Journal, 33:5, 1991, 12-17.

- Rodhal, E.: The point of separation for cold jets flowing along the ceiling, CLIMA 2000 Conference, Belgrade, Yugoslavia, 1977, 219-228.

GLOBALNI PRISTUP KVALITETI KLIMATIZIRANOG UNUTARNJEG PROSTORA: TOPLINSKI KOMFOR, 
ZVUČNI KOMFOR, KVALITETA DIFUZIJE ZRAKA

Sažetak: Predstavljena je eksperimentalna studija na izvedenom sustavu hlađenja, ventilacije i klimatizacije te njegova optimizacija u svrhu smanjenja lokalne nelagodnosti u klima komori. Najprije su analizirane osnovne karakteristike kao što je udaljenost razdvajanja mlazova na hladnom zidu te maksimalna brzina i pad temperature. Nakon toga analizirana je nelagodnost uzrokovana toplinskim utjecajem, utjecajem zvuka te utjecajem difuzije zraka u skladu s karakteristikama strujanja zraka. Uključen je i ekonomski parametar u svrhu prikazivanja generalnog pristupa globalnoj lagodnosti.

Ključne riječi: klimatizirani uredi, horizontalni mlaz toploga zraka, toplinska lagodnost, zvučna lagodnost, kvaliteta difuzije zraka, eksperiment, sustav hlađenja, ventilacije i klimatizacije