FEASIBILITY STUDY OF OFFSHORE AND ONSHORE

WIND PLANTS FOR INSTALLATION IN CROATIA

ALONG THE ADRIATIC SEA

Lj. Pilić-Rabadan, B. Klarin, M. Sansević-Novaković

University of Split, Faculty of Electrical and Mechanical Engineering and Naval Arch.

R.Boškovića b.b., 21000 Split, CROATIA

Tel.: ++385-21-305-777	Fax.: ++385-21-563-877

Abstract: This paper focuses on economic and technological factors relative to the construction and operation of offshore and onshore wind plants in Croatia along the Adriatic Sea. Similar wind power plants in Europe will be taken into consideration. With the increasingly rapid development of construction technology of offshore and onshore wind power plants, costs in these types of installations are expected to decrease. This fact offers the possibility of exploiting offshore and onshore wind potential in Croatia in the near future.

This study assesses the quality of possible offshore sites using the existing data. For this reason, there is a need for additional examination of wind potential by using contemporary procedures as well as selecting sites by means of a collaborative effort.

The first analysis carried out affords a global overview of possible exploitation of wind in wind plants in Croatian Adriatic Sea areas as an initial step pointing to the potential of this branch of wind energy.

Keywords: offshore wind plant, onshore wind plant

1. INTRODUCTION

Owing to the successful operational results of five wind plants installed offshore in territorial waters of Denmark, the Netherlands and Sweden, Table 1, Ref. [1], five other offshore plants have been planned. They are likely to be built at the beginning of the 21st century.

The reasons for using sea areas for offshore wind power plants are as follows: higher wind potential (in principle) than on land where the wind turbine axis is installed at a lower sea level; underdeveloped areas of state-owned property; development in technology concerning the foundation and cable connections and wind turbine technology designed for operation offshore.

Table 1. Basic Data of Offshore Wind Plants at Work, Ref. [1]

| Location | Start | No. units | Capacity | Wind | Output | Cost | Cost/ |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | date | n x kW | MW | speed m/s | GWh (Est./actuall) | $million | output $/MWh |
| Lely | 1995 | 4 x 500 | 4.00 | - | - | - | - |
| Norgesund | 1990 | 1 x 220 | 0.22 | - | - | - | - |
| Scroby | planned | 25 x 1500 | 37.50 | 8.0* | 98* | 53.0 | 540.00 |
| Tuno | 1995 | 10 x 500 | 5.00 | 7.4* | 12.5/12.7 | 13.0 | 1,040.00 |
| Vindeby | 1991 | 11 x 450 | 4.95 | 7.9* | 11.2/11.73 | 12.7 | 1,134.00 |
| Comparable onshore farm in 1991 |  |  |  | 7.2 | 10 | 7.0 | 700.00 |

* Author's estimate (Milborrow D.)

2. ASSESSMENT OF TECHNICAL WIND POTENTIAL FOR OFFSHORE AND ONSHORE POWER PLANTS

The estimate of technically exploitable wind potential in the region of the Croatian Adriatic Sea and coastal area is based on: estimation of natural wind energy potential with regard to the distance from land; height above sea level; selection of wind plant sites as a function of a number of evaluation parameters and selection of a wind energy technology for offshore and onshore wind plants. In the final choice of offshore and onshore wind plants, Ref.[2], the basic ranking parameters are maximum electric energy and minimum cost for the expected operation time. According to the European Wind Atlas, Ref.[3], wind potential in the vast Mediterranean region, including the Croatian Adriatic Sea as well, is similar and ranges from 4.5 to 7 m/s at an altitude of 10 m.

The first wind potential estimate in the region of the Adriatic Sea as a whole was issued in Ref.[4], Fig.2, by Croatian authors on the basis of meteorological measurements on the mainland and islands. Wind rose cards, based on data gathered by observation on ships and meteorological stations on the mainland, were issued in 1979, Ref.[5]. The comparison of the above-mentioned wind potential serves as the basis for the analysis of wind potential of the Croatian Adriatic Sea and coastal area.

The offshore zone, 10 km from the Croatian coast and at an altitude of 10 m, has a specific wind power of 250 to 300 W/m2, which corresponds to a wind speed of 6 to 7 m/s at the same altitude. As a comparison, offshore wind plants in Denmark operate at wind speeds of up to 8 m/s 15 km from the coast, whereas 40 km from the coast wind is being increased up to 8.5 m/s, Ref.[3]. In choosing a site closer to the coast it is necessary to investigate, in particular, the impact of the mainland.

Figure 1. Specific Wind Power of the Adriatic Sea in W/m2 at an Altitude of 10 m Facing Poje and Cividini, Ref.[4].

3. SELECTION OF SITES FOR OFFSHORE AND ONSHORE WIND PLANTS AND TECHNICAL WIND POTENTIAL

3.1. Criteria for Selecting Offshore and Onshore Wind Plant Sites

In choosing offshore and onshore wind plant sites, a number of criteria should be taken into consideration; some of these are also used for wind plants on the mainland, whereas other specific criteria for offshore and onshore wind plants are given in Refs. [6] and [7].

Areas which should be exempted from offshore and onshore wind plants are national parks and protected ecological areas, areas used for navigation and mooring, specific purpose areas (military zones, etc.), and tourist facilities (hotels, marinas, etc.). Criteria determining the suitability of a site for wind plant installation include power system, design, ecology and zoning. Apart from the wind potential, sea depth as well as distance from the coast are also important.

Installation of wind plants depends upon the depth of the sea: units are set up on concrete or metal structures fixed to the sea bottom at depths up to 50 m. For depths greater than 50 m,  units are fixed to buoys. The distance of the offshore wind plant site from the shore affects the costs of the cable connection, therefore increasing investment costs.

The size of the site is of considerable importance; notably, the greater the number of wind plant units, the lower specific costs. It is worth pointing out that wind turbine units in offshore plants are sited at greater distances one from another than in onshore wind plants due to the greater impact of the turbine to the wake; therefore, larger offshore sites are needed.

The installation of offshore and onshore wind plants does not act considerably upon the fauna, particularly upon birds and their migration or fish. The countryside is less affected if the site is located farther from the coast. More suitable sites are placed far away from settlements and tourist facilities.

Maintenance of offshore and onshore plants is dependent upon the accessibility to the site as well as difficulties that may arise from bad weather conditions.

3.2. Selecting Sites for Offshore and Onshore Wind Power Plants in Croatia

According to the layout of wind potential, the Croatian Adriatic Sea is situated between two wind energy regions; that one in the South Adriatic is estimated to be more valuable. Therefore, the selection of the location for offshore and onshore plants may be confined to that region.

As is pointed out in Item 2.1., the sea depth plays an important part in selection of offshore and onshore power plants location. It is therefore necessary to analyze the batimetric chart of the South Adriatic Sea. The sea depth rapidly increases from the shore, and areas with a depth of up to 50 m are very close to the coast and islands respectively. Apart from this, these areas are situated within the intensive navigational zone (e.g.the Split and Neretva Channels). Therefore, it is not possible to set up a great number of wind turbine units on either gravity-based concrete foundations or metal structures resting on the sea bottom. There is, however, a possibility to place wind turbine units upon the shallows and rocks, but this consideration should be particularly examined with respect to the inclination of the sea bottom and accessibility to the location itself. Therefore, the eventual offshore power plant sites would have a depth of more than 50 m, which means that wind turbine units would be placed on floating structures. So, in order to make the cost of the wind power plants connection to the power grid as low as possible, the offshore power plant should be situated very close to the coast or islands. Since areas between the mainland and islands, as well as interinsular areas, are used for navigation, it seems more suitable for wind turbines to be installed around islands farthest from the coast, in particular, at their outer sides. Consequently, the most suitable locations for offshore installations could be areas near the Island of Vis and the Island of Lastovo. Figure 2. shows areas near the Island of Vis (LOCATION I) and the Island of Lastovo (LOCATION II) suitable for installation of wind turbines, according to Ref.[8].

Figure 2. Feasible Sites for Offshore Plants in the Vicinity of the Islands of Vis (I) and Lastovo (II), Ref.[8].

There are capes and shallows suitable for building dikes and installing turbine units in onshore plants. A number of wind turbines could be placed in capes while embankments, Figure 3, could serve as breakwaters or for mooring.

Figure 3. Onshore Wind Plants with Wind Turbines Having a Nominal Power of 55 kW, Ebeltoft, Denmark

3.3 Assessment of Technical Wind Potential for Offshore and Onshore Wind Plants

While analyzing wind potential at an altitude of 50 m for the South Adriatic Sea, it was found that the values of the annual mean wind speeds amount to 7.0 and 8.0 m/s, and the specific mean wind power ranges from 400 to 600 W/m2. Supposing that the average of these amounts is an average for the South Adriatic Sea, the mean speed can, thus, be taken to be 7.5 m/s and specific mean power 500 W/m2. As these data were taken as parameters of Weilbull distribution, it was necessary to make altitude corrections of this curve according to logarithm rule. In this way, average annual speeds at altitudes of 10, 25, 50 and 100 m have been obtained and they have been taken as input data for simulation of wind turbine operation at chosen offshore plants.

3.4. Simulation Results for Offshore Wind Power Plants

For the simulation of the operation of wind turbine units in offshore plants, two modern machines of 750 kW and 1000 kW have been taken from the data base of the expert system CRO-EOL, Ref.[2], having the characteristics shown in Table 2.

Table 2. Basic Technical Characteristics of Selected Wind Turbines with 750 and 1000 kW of Nominal Power, Ref.[2]

| Wind Turbine Power | Unit | 750 kW | 1000 kW |
| --- | --- | --- | --- |
| Height of Axis | m | 51 | 55 |
| Diametar | m | 43.4 | 54 |
| Generator Type |  | Asynchronous | Asynchronous; 6/4 poles |
| Rotation | rpm | 32.5 | 16.2/24.4 |
| Blades | / | 2 | 3 |
| v in,v rat, v out | m/s | 4, 14.5, 22 | 4, 13.5, 28 |
| Regulation | / | pitch | pitch |
| Voltage | V | 690 | 690 |
| Grid Frequency | Hz | 501% | 50 |

Simulation of electricity production by selected machines is brought about by multiplicating the duration of individual speeds from Weibull distribution by the output power of a turbine unit, whereas the annual electricity production is obtained by their addition, Ref.[9]. The results obtained for units of selected wind turbines at an altitude of 51 m for a 750 kW machine and at 54 m for a 1000 kW machine, are shown in Table 3, Ref.[8].

Table 3. Operational Simulation Results of 750 kW and 1000 kW Machines (specific energy by kW; specific energy by m2; capacitance; potential annual energy production by wind turbine unit), Ref.[8]

| WT power kW | kWh/kW | kWh/m2 | Cf | MWh/year |
| --- | --- | --- | --- | --- |
| 750 | 2,238.34 | 1,135.00 | 0.2553 | 1,678.76 |
| 1000 | 2,503.77 | 1,093.00 | 0.2856 | 2,503.77 |

Due to favourable conditions for building offshore and onshore plants, which also include the possibility of building an additional number of wind turbines, the number of wind turbine units installed in offshore and onshore plants as well as their production can be calculated. Table 4. provides an overview of potential annual production of a great number of units in offshore plants on the basis of the estimate given in Table 3.

Table 4. Potential Annual Production in GWh of a Group of Wind Turbine Units with 750 or 1000 kW of Nominal Generator Power in Offshore Plants, Ref.[8].

|  | Potential annual electricity production |  |
| --- | --- | --- |
| Possible number of WT | 750 kW GWh/god | 1000 kW GWh/god |
| 10 | 16.8 | 25.0 |
| 20 | 33.6 | 50.0 |
| 50 | 83.9 | 125.0 |

4. TECHNICAL AND COST ASPECTS OF OFFSHORE AND ONSHORE WIND PLANTS

As to design, wind turbines for offshore and onshore plants differ slightly from those used for power plants on the mainland. The distinction refers particularly to the protection of the generator from sea dust, the positioning of the transformer and circuit breaker inside the tower and a greater number of cranes. Small technical changes which should be undertaken and which do not affect the cost of the wind turbine concern the adjustment of the wheel rotation speed in order to obtain greater wind energy potential. A particularity of an offshore wind plant is a support which has to withstand loads of both the sea current and waves.

The sea depth affects the following types of (platforms) supports:

a) gravity-based concrete foundation - sunken foundation block is filled with ballast. It is applicable to depths from 3 to 5 m, and to a maximum from 15 to 20 m

b) metal-concrete structures - arms of the platform are dug into the sea bottom and anchored;

c) floating structure - it is anchored to greater sea depths

The last two types have been developed for the extraction of oil and gas from the sea; they have been, so far, considered as possibilities for offshore plant installation at greater depths, Ref.[10]. Figure 4. provides a layout of offshore/onshore wind power plant foundations.

| FOUNDATIONS |  |  |  |  |
| --- | --- | --- | --- | --- |
| OFFSHORE WIND PLANT |  |  | ONSHORE WIND PLANT |  |
| concrete-ballast | metal-concrete | floating | embankment | standard |
| gravity-based | gravity-based |  |  |  |

Figure 4. Design Feasibilities of Offshore/Onshore Wind Power Plant Foundations

Other peculiarities concerning offshore wind power plants refer to preparatory works, wind turbine installation on the site by means of floating cranes and its connection to the grid on the mainland by submarine cables.

The cost analysis of a 5 MW offshore wind plant, Figure 5., according to Ref.[11], sited 3 to 6 km from the coast at a depth of <6 m shows that the costs of the foundation, installation and connection to the grid are equal to those of the wind turbine itself. With (standard) turbines on the mainland the costs are considerably lower.

Figure 5. Layout of Relative Costs for Offshore and Turbines on the Mainland Compared to Unit Costs of Wind Turbines

The specific capital costs of the first offshore wind power plants built from 1991 to 1995 (data are given in Figure 5.) were 2100-2300 USD/kW; average costs for wind turbines on the mainland, by contrast, were 1000-1350 USD/kW, Refs.[7] and [10]. Considering the study analysis of construction costs of new wind plants sited at greater distances from the coast (15-30 km) and greater depths (up to 15 m), construction costs of offshore wind power plants, Ref.[12], are expected to decrease by 25%. Notably, capital costs would be 1600-1800 USD/kW.

Compared to wind plants on the mainland, offshore/onshore wind plants require greater investment and maintenance costs. With regard to the fact that a relatively small number of similar wind plants have been built so far, investment costs increase by approximately 60-85% and maintenance costs by 50% in comparison with the same costs for wind plants on the mainland.

Consequently, general guidelines concerning the design of offshore and onshore wind power plants in the Croatian Adriatic Sea should include: wind generators of greater unit power (  1 MW); installation in shallow waters (less expensive technique of gravity based foundations is applicable) as close as to the mainland or islands as possible (reduced connection costs to the grid).

Metal-concrete structures are, for lesser depths, 20-40% more expensive than the foundation technique of wind generators for offshore/onshore plants applied to date. In floating structures, construction, anchoring and connection costs for depths of 100 m are estimated to be 60% of the entire power plant price against 18% of the wind generator share. Investment costs for a 12 MW offshore wind plant, in floating structure design, according to Ref.[10] amount to 3900 USD/kW.

CONCLUSION

- according to wind charts for territorial waters of European countries, Ref.[13] and a chart from Ref.[4] concerning the territorial waters of the Republic of Croatia, at the axis height of modern wind turbine units, we can count on wind potential being greater than on selected macrolocations on the mainland. This wind potential corresponds, according to available data, to the average wind potential of the sea area of other Mediterranean countries.

- conversion of wind energy into electric energy has been simulated on the already mentioned foundation at the axis height of modern 750 kW and 1000 kW units. The energy yield is 1,678,76 MWh/year for the 750 kW unit and 2,503.77 MWh/year for the 1000 kW unit.

- economic factors relative to construction and operation of offshore and onshore wind power plants are based on experiences of five wind plants of the same type in three European countries. It can be observed that capital investment and power generation cost of offshore wind plants for the period of five years, have been in decline. It is due to development of new equipment which, on the basis of operational experience, are of better quality.

- installation of offshore wind power plants near the Islands of Vis and Lastovo, where sea depths close to the islands reach 100 m, would require foundations to be either metal-concrete gravity based structures or anchored floating structures.

- the analysis of a potential wind energy conversion in Croatian offshore and onshore wind power plants is an initial step indicating the prospects of this branch of wind power energy, Ref.[8].

REFERENCES

[1] Milborrow, D.: Offshore Wind Plants and Developments, Wind Stats Newsletter, Vol.9 (1996) No.4.

2 Pilić-Rabadan Lj., Milas Z., Stipaničev D., Jelavić M., Vujčić R., Klarin B., Sansević M.: Use of expert systems in wind turbine applications, Proc. European Community Wind Energy Conference and Exhibition, Lübeck, 1993, 804-807.

###### [3] Petersen, E.L., Mortensen, N.G., Landberg, L.: Wind resource estimation and siting of wind turbines, European Directory of Renewable Energy 1994, James & James, 1994.

###### [4] Poje D., Cividini B.: Assesment of wind energy potential in Croatia, Solar Energy, Vol. 41 (1988) 6; 543-554.

[5] Klimatološki atlas Jadranskog mora, Hidrografski Institut HRM, 1979.

6 Botta, G., Ciancio, E., Grego, G., Leotta, A.: Assessment of Italian off-shore wind resources, Proc. Offshore Wind Energy in Mediterranean and other European Seas, Rome, 1994, 63-71.

8 Pilić-Rabadan, Lj., Klarin, B., Sansević-Novaković, M., Milas, Z.: Analiza tehničkog potencijala vjetra na obali i otocima Hrvatske, FESB, Institut "Hrvoje Požar", Zagreb, 1998.

7 Gaudiosi G.: Offshore wind energy potential in the Mediterranean, Proc. 2nd World Renewable Congress, Reading, 1993, 1622-1633.

9 Klarin B.: Izbor optimalne vjetroturbine pomoću ekspertnog sustava - magistarski rad, FSB, Zagreb, 1995.

10 Tong K.C.: Techical and Economical Aspects of a Floating Offshore Wind farm, Proc. Offshore Energy in Mediterennean and other European Seas, 1994, 167-178.

11 Olsen F.A., Rasmussen K.J.: Vindeby Offshore Wind Farm, Proc. Offshore Energy in Mediterennean and other European Seas, 1994, 189-203.

[12] Madsen, B.T.: 4000 MW of Offshore Wind Power by 2030, Wind Stats Newsletter, Vol.10 (1997), No.3.

[13] Madsen, B.T.: Wind's Share in Global Energy Markets, Wind Stats Newsletter, Vol.10 (1997), No.3.

ANALIZA MOGUĆNOSTI POSTAVLJANJA POMORSKIH I OBALNIH VJETROELEKTRANA NA HRVATSKOM DIJELU

JADRANSKOG MORA

Sažetak: U ovom radu analizirani su gospodarski i tehno-ekonomski čimbenici izgradnje i rada offshore i onshore vjetroelektrana na Hrvatskom dijelu Jadranskog mora a na temelju iskustva izgradnje i rada postojećih vjetroelektrana ovih vrsta u Europi. Razvojem tehnologije izgradnje offshore i onshore vjetroelektrana predviđen je do pad cijena instalirane snage u ovakvim postrojenjima. Ova činjenica ukazuje na mogućnost budućeg korištenja vjetropotencijala na morskoj pučini i samoj obali Hrvatske.

U radu je dana procjena kvalitete mogućih prostora na moru koja se oslanja na postojeće podatke. U ovu svrhu potrebno je dodatno ispitati vjetropotencijale suvremenim postupcim i izabrati lokacije pomoću suradničkog ekspertnog sustava.

Provedena prva analiza daje globalni prikaz mogućnosti korištenja vjetra u vjetroelektranama na morskom prostoru Hrvatske kao početni korak koji ukazuje na perspektive u ovoj grani vjetroenergetike.